## Data
LM6000 Data | Units | Sample Data | CTG 1 | CTG 2 | Notes
Start Time |  | 2009-10-03 14:00
End Time |  | 2009-10-03 15:00
Dry Bulb Temperature | Deg F | 86
Relative Humidity | % | 47
Barometric Pressure | Psia | 14.48
Selected Control Mode (T3 ,PS3, T48, Etc.) | -- | T48
Generator Gross Output | MW | 50.751
Panel Readout MVAR | Mvar | 24.5798
Generator Power Factor (Panel) | -- | 0.9
Generator Power Factor (Calc) | --- | 0.9 | #DIV/0! | #DIV/0!
Generator Frequency | Hz | 60
HP Compressor Speed (Selected) | RPM | 10450 |  |  |  | Yellow highlight required for overall compressor efficiency
LP Compressor Speed (Selected) | RPM | 3600 |  |  |  | Orange highlight required for LP/HP compressor efficiency breakout
T2 SEL - Compressor Inlet Temperature | Deg F | 46
T25 SEL - H.P. Comp Inlet Temp | Deg F | 220
T3 SEL - H.P. Comp Disch Temp (CTD) | Deg F | 983.1
T48 AVG - L.P. Turbine Inlet Temp | Deg F | 1600
P0 - L.P. Comp Inlet Press | Psia | 14.2995
P0 - Calculated (Barom - Inlet Losses) | Psia | 14.2995
P25 SEL - H.P. Comp Inlet Press | Psia | 30
PS3 SEL - H.P. Comp Disch Press | Psia | 459.5
PTB SEL - Thrust Balance Press | Psia | 25
P48 SEL - L.P. Turbine Inlet Press | Psia | 250
VBV Position | % | 0
VSV Position | % | 100
Fuel Gas Flow ACFM | ACFM | 181.5
Fuel Gas Flow SCFM | SCFM | 7628.6
Fuel Gas Pressure | Psig | 550
Fuel Gas Temperature | Deg F | 60
Nox Water Injection Flow | GPM | 41.3 |  |  | we only need one of them
Nox Water Injection Flow | PPH | 20516 |  |  | we can calculate the other
Static Inlet Loss | In H2O | 5 |  |  | if available (DP across the filters)
Static Exhaust Loss | In H2O | 12 |  |  | if available (DP across the exhaust SCR, steam generator, etc.)
CEMS NOx Emissions | PPM | 2.6
CEMS CO Emissions | PPM | 0.1
Engine Fired Hours | Hours | 200
Gas - BTU (HHV) | Btu/SCF | 1047
Gas - Gravity | -- | 0.65
Gas - Mole Fraction Carbon Dioxide (CO2) | mole% | 0.93
Gas - Mole Fraction Nitrogen (N2) | mole% | 5.93
Gas - Mole Fraction Methane (CH4) | mole% | 84
Gas - Mole Fraction Ethane (C2) | mole% | 5.58
Gas - Mole Fraction Propane (C3) | mole% | 2.05
Gas - Mole Fraction Isobutane (iC4) | mole% | 0.78
Gas - Mole Fraction n-Butane (nC4) | mole% | 0
Gas - Mole Fraction Isopentane (iC5) | mole% | 0.18
Gas - Mole Fraction n-Pentane (nC5) | mole% | 0
Gas - Mole Fraction neo-Pentane (neoC5) | mole% | 0
Gas - Mole Fraction Hexane (C6) | mole% | 0.17
Gas - Mole Fraction Hydrogen Sulfide (H2S) | mole% | 0
Gas - Mole Fraction Hydrogen (H2) | mole% | 0
Gas - Mole Fraction Oxygen (O2) | mole% | 0.14
Gas - Mole Fraction Helium (He) | mole% | 0
Gas - Mole Fraction Argon (Ar) | mole% | 0
Gas - Mole Fraction Carbon Monoxide (CO) | mole% | 0
Gas - Delivery Pressure | Psia | 550
Gas - Delivery Temperature | Deg F | 60
Gas - Total Delivered Fuel Flow | SCFM | 7630